## Slide 1
Special keywords for the Commissioning of the
Screw units at Krasnador
Read Operating Instruction SB-110-1
delivered with the compressor
Electrical Connection
First Start-up Procedure

## Slide 2
Electrical Connection
  Check voltage and frequency data on nameplate
  Wiring according to the instructions in the terminal box cover
  Screw Compressors may only be operated in one direction of rotation!
  Terminals 1-5/B1-B2/T1-T2 must not come into contact with control voltage
  Part-Winding motor
    Time delay 0,5s
    Wrong wiring leads to locked rotor conditions
  Check wiring and function of safety devices
    SE-B2 and INT389R
    Oil flow switch
    Pressure controls (HP&LP)
    Components for oil separator
Notes: E:\appl_limits\recip\eg_kv_e.ppt

## Slide 3
Leak test (dry nitrogen)
Oil charging: Direct charging into oil separator & oil cooler Quantity: Oil volume OS + OC + oil lines + small quantity for circuit (1-2% of total refrigerant charge)
Caution! Only use BITZER approved lubricants
Evacuation
  generously sized additional connections
  open shut off and solenoid valves (not oil solenoid!!)
  Check valves: possibly By-pass or separate connections
  Caution! Never start under vacuum
Notes: After all piping work has been done one has to fill up the oil separator with oil. In the extent of delivery of the oil separator there are such components like heater, thermostat and oil level control. All these parts are not assemble by us, because of the high risk that during transport these parts can be damaged. The oil will be filled through the oil filling connection into the oil separator until the oil level has reach the middle of the sight glass. If the oil separator is above the oil cooler also the cooler can be filled with oil.
Important!
The oil solenoid valve must be closed during the filling process.
Next step is the pressure test, preferable with dry nytrogen. Afterwards one can start with the evacuation of the whole circuit,
Because there is at least one checkvalve (compressor) it is recommend toconnect the lines to the vaccum pump on different positions or to bypass the checkvalve.
On the first view one could believe thinking vacuum is a good insulation. This is true for the heat transfer, but the lower the pressure the worse in respect of the dielectricity. Spo please never start a compressor in vacuum because this can cause a heavy short circuit.

## Slide 4
Refrigerant charging
  check oil level & function of oil heater
  liquid charging into receiver, condenser and flooded evaporator
  topping during operation -- via suction side
  Take care upon operating limits with under-charged system!!
Checking before start
  oil level (within sight glass range)
  oil temperature (15...20 K above ambient temperature)
  checking of safety devices (motor fuses removed)
  set point values of timing relays
Attention! In case of flooding the compressor with oil --
remove at oil intake connection!
Notes: Therefore the next step is to fill refrigerant into the system. But before starting with the filling also the heater in the oil separator can be switched on.
In case the oil separator is installed out side the machining room, it is strictly recommended to insulate the oil separator. The refrigerant normally will be filled into the receiver, sometimes, on a flooded system, also into the evaporator.
What can we do, when by an accident the compressor was filled up with oil.
It is clear you have to drain the oil out of the compressor. There are two possibilities either you can open the connection on the pipes or the endcover can be removed. Then there is the possibility to turn the rotors by hand and you are sure that there is no oil inside of the machine.
For sure you know from your own experience that very often one has filled not enough refrigerant into the circuit which means the suction pressure went done and has to top up the circuit. This will be done in most cases on the suction-side, but only when the compressor is in operation.

## Slide 5
Starting of compressor No 1
  Disconnect CR2, 3 and 4
  Replace CR2 and CR4 coil by using Danfoss Magnets
  Check the direction of rotation -- by briefly (0.5 ... 1 sec) starting the compressor (suction shut off valve almost closed)
  Control with suction gauge
  If required, reverse phase sequence on common compressor supply
Notes: In my eyes we are coming now to one of the most important points during the commision phase. The compressor can run only in one direction. Operation in wrong direction for some seconds will destroy the compressor. Of course we have a protection device which should prevent the operation in the wrong direction. Also the compressor had made a test run, so we are sure that the cable inside of the motor were connected in the properway. However some customer like to install the protection devices in the switchboard. Also our are people are human beings so we can never exclude that also we make a mistake. Therefore a double control is recommended.
On open compressors the situation is much better. There we can separte both coupling halves so the motor can run without compressor. We press the contactor for a second and one can see immediataly if the pressure went down or not. The same procedure should be repeated with the second contactor.

## Slide 6
Repeat start, open shut off valve slowly.
  Adjust suction shut off valve to reach suction pressure (temperature) below 0°C. At 50% capacity, short time operation above HSN- application limit up to 0°C is possible. Danfoss magnets still at CR2 and 4.
  If the compressor stops by oil flow, remove Danfoss magnet from CR4, change the second magnet from CR2 to CR3. Wait for 5 minutes delay time. Change the magnets back to CR2 and 4. Start the compressor, adjust suction temperature to -10°C. (Higher pressure difference = more oil flow)
  Check function of LP and HP switch, test wiring of SE-E2 by disconnecting Motor PTC, stop oil flow by hand to check function of flow switch and oil stop valve.
Notes: When opening the shut off valve slowly on one side this offers a small protectionagainst liquid slugging on the other side by this measurement we reached qiute easy a certain pressure difference which is important for the oil flow.

## Slide 7
  Oil level control in oil separator sight glass
    slight foaming possible (should tend to disappear after 2..3 min)
    discharge gas temperature min. 30 K above SCT
    switching of flow or level control is a sign for serious oil fault.
  Run the compressor to pull down the low pressure receiver below -10°C.
  Open suction shut off valve complete.
Notes: When opening the shut off valve slowly on one side this offers a small protectionagainst liquid slugging on the other side by this measurement we reached qiute easy a certain pressure difference which is important for the oil flow.

## Slide 8
Starting of compressor No 2 and 3 by the same steps
  Disconnect CR2, 3 and 4
  Replace CR2 and CR4 coil by using Danfoss Magnets
  Check the direction of rotation -- by briefly (0.5 ... 1 sec) starting the compressor (suction shut off valve almost closed)
  Control with suction gauge
  If required, reverse phase sequence on common compressor supply
Notes: In my eyes we are coming now to one of the most important points during the commision phase. The compressor can run only in one direction. Operation in wrong direction for some seconds will destroy the compressor. Of course we have a protection device which should prevent the operation in the wrong direction. Also the compressor had made a test run, so we are sure that the cable inside of the motor were connected in the properway. However some customer like to install the protection devices in the switchboard. Also our are people are human beings so we can never exclude that also we make a mistake. Therefore a double control is recommended.
On open compressors the situation is much better. There we can separte both coupling halves so the motor can run without compressor. We press the contactor for a second and one can see immediataly if the pressure went down or not. The same procedure should be repeated with the second contactor.

## Slide 9
Setting / Control of oil temperature regulating device
  cooling effect must not start, before oil temperature has not reached a level of approx. 25..30 K above SCT
  max. setting temperature 80°C
Vibrations
  If necessary additional protective measures must be taken

## Slide 10
Setting / Control of condenser pressure regulation
Checking of operating conditions
  SST + suction superheat
  SCT + liquid temperature
  Eco + suction superheat
  discharge gas temperature
  oil temperature
  Current/ voltage
Fill in complete measuring report.
Compare measured data with data from Bitzer Software.